## $ per kVA Vs Cents per kWh
Western Power's Distribution Network Costs ($/kVA/yr) Verses Network Tariffs (Cents/kWh)
For Customer Groups used in the Distribution System Cost of Supply
Based on 2016/17 Price List Information Published by Western Power DM# 13828866
Distribution Customer Group Information from Table 15 (Page 51) 2016/17 Price List Info
| GWh | Customers | LV Only Customers | ATMD (MVA) | ATMD - HV Network (MVA) | ATMD Transformers (MVA) | ATMD- LV Network (MVA)
Unreads | 33 | 17421 | 17421 | 5 | 6 | 6 | 6
Streetlights | 140 | 267109 | 267109 | 33 | 36 | 36 | 4
Residential | 5183 | 1013751 | 1013751 | 1912 | 2072 | 2072 | 2072
Small Business | 906 | 73544 | 73544 | 336 | 351 | 351 | 351
General Business -Small | 1122 | 12957 | 12957 | 554 | 579 | 579 | 579
General Business -Med | 1126 | 2911 | 2620 | 490 | 513 | 513 | 461
General Business-Large | 1217 | 964 | 96 | 467 | 483 | 483 | 48
LV >1000kVA | 377 | 125 | 13 | 168 | 174 | 174 | 17
HV less that 1000kVA | 257 | 116 | 0 | 63 | 64 | 0 | 0
HV > 1000kVA | 2837 | 316 | 0 | 844 | 862 | 0 | 0
Total | 13198 | 1389214 | 1387511 | 4872 | 5140 | 4214 | 3538
Distribution Customer Allocated Costs by Distribution Cost Type from Table 10 (Page 24) 2016/17 Price List Info
| HV Network Fixed ($M) | HV Network Variable ($M) | LV Network Fixed ($M) | LV Network Variable ($M) | Trxs Variable ($M) | Streetlights ($M) | Metering ($M) | Admin ($M) | Total ($M)
Unreads | 2.1 | 0.4 | 1.4 | 0.3 | 0.2 | 0 | 0 | 0.6 | 5
Streetlights | 3.7 | 2.5 | 2.1 | 0.2 | 1.3 | 28.1 | 0 | 1.9 | 39.8
Residential | 134.1 | 143.2 | 80.1 | 110.6 | 75.5 | 0 | 51.3 | 97.7 | 692.5
Small Business | 13.6 | 26.6 | 6 | 18.7 | 13.4 | 0 | 7.4 | 14.5 | 100.2
General Business -Small | 2.2 | 44.8 | 1.1 | 31 | 22.5 | 0 | 4.1 | 21 | 126.7
General Business -Med | 0.5 | 38.8 | 0.2 | 24.6 | 19.7 | 0 | 2.4 | 18.4 | 104.6
General Business-Large | 0.2 | 33.8 | 0 | 2.6 | 17.8 | 0 | 1.2 | 17.5 | 73.1
LV >1000kVA | 3.7 | 14.8 | 0 | 0.9 | 6.7 | 0 | 0.2 | 2.3 | 28.6
HV less that 1000kVA | 0 | 4.1 | 0 | 0 | 0 | 0 | 0.4 | 2.4 | 6.9
HV > 1000kVA | 21.6 | 38.2 | 0 | 0 | 0 | 0 | 1.2 | 6 | 67
Total | 181.7 | 347.2 | 90.9 | 188.9 | 157.1 | 28.1 | 68.2 | 182.3 | 1244.4
Distribution Customer Group Costs and Alternative Tariffs ($/Customer and $/kVA)
| HV Fixed $/Cust/yr | HV Variable $/kVA/yr | LV Fixed $/Cust/yr | LV Variable $/kVA/yr | Trxs Variable $/kVA/yr | Streetlights $/Cust ??? | Metering $/Cust/yr | Admin $/kVA/yr |  | Dist Total Fixed $/Cust/yr | Dist Total Variable $/kVA/yr | Customers | ATMD (MVA) | Ave ATMD/ Customer (kVA) | Dist Total Fixed Costs ($M) | Dist Total Variable Costs ($M) | Total Revenue ($M)
Unreads | 120.5442 | 80 | 80.3628 | 60 | 40 | 0 |  | 120 |  | 200.907 | 300 | 17421 | 5 | 28.701 | 3.5 | 1.5 | 5
Streetlights | 13.852 | 75.7576 | 7.862 | 6.0606 | 39.3939 | 105.2005 | 0 | 57.5758 |  | 126.9145 | 178.7879 | 267109 | 33 | 12.3545 | 33.9 | 5.9 | 39.8
Residential | 132.281 | 74.8954 | 79.0135 | 57.8452 | 39.4874 | 0 | 50.6041 | 51.0983 |  | 261.8986 | 223.3264 | 1013751 | 1912 | 1.8861 | 265.5 | 427 | 692.5
Small Business | 184.9233 | 79.1667 | 81.5838 | 55.6548 | 39.881 | 0 | 100.62 | 43.1548 |  | 367.1272 | 217.8571 | 73544 | 336 | 4.5687 | 27 | 73.2 | 100.2
General Business -Small | 169.7924 | 80.8664 | 84.8962 | 55.9567 | 40.6137 | 0 | 316.4313 | 37.9061 |  | 571.1199 | 215.343 | 12957 | 554 | 42.7568 | 7.4 | 119.3 | 126.7
General Business -Med | 171.7623 | 79.1837 | 76.3359 | 50.2041 | 40.2041 | 0 | 824.4589 | 37.551 |  | 1072.5571 | 207.1429 | 2911 | 490 | 168.327 | 3.1222 | 101.5 | 104.6222
General Business-Large | 207.4689 | 72.3769 | 0 | 5.5675 | 38.1156 | 0 | 1244.8133 | 37.4732 |  | 1452.2822 | 153.5332 | 964 | 467 | 484.4398 | 1.4 | 71.7 | 73.1
LV >1000kVA | 29600 | 88.0952 | 0 | 5.3571 | 39.881 | 0 | 1600 | 13.6905 |  | 31200 | 147.0238 | 125 | 168 | 1344 | 3.9 | 24.7 | 28.6
HV less that 1000kVA | 0 | 65.0794 | 0 | 0 | 0 | 0 | 3448.2759 | 38.0952 |  | 3448.2759 | 103.1746 | 116 | 63 | 543.1034 | 0.4 | 6.5 | 6.9
HV > 1000kVA | 68354.4304 | 45.2607 | 0 | 0 | 0 | 0 | 3797.4684 | 7.109 |  | 72151.8987 | 52.3697 | 316 | 844 | 2670.8861 | 22.8 | 44.2 | 67
Average | 130.7934 | 71.2644 | 65.513 | 38.7726 | 32.2455 | 20.2521 | 49.0925 | 37.4179 |  | 265.651 | 179.7003 | 1389214 | 4872 | 3.507 | 368.9222 | 875.5 | 1244.4222
Check
Distribution Customer Group Implied Tariffs ($/Customer and Cents/kWh) based on 2016/17 Price List Info
| HV Fixed $/Cust/yr | HV Variable c/kWh | LV Fixed $/Cust/yr | LV Variable c/kwh | Trxs Variable c/kwh | Streetlights $/Cust/yr ??? | Metering $/Cust/yr | Admin c/kwh |  | Dist Total Fixed $/Cust/yr | Dist Total Variable Cents/kWh | Customers | GWh | Ave kWh/ Customer | Dist Total Fixed Costs ($M) | Dist Total Variable Costs ($M) | Total Revenue ($M)
Unreads | 120.5442 | 1.2121 | 80.3628 | 0.90909 | 0.60606 | 0 | 0 | 1.8182 |  | 200.907 | 4.5455 | 17421 | 33 | 189.4266 | 3.5 | 1.5 | 5
Streetlights | 13.852 | 1.7857 | 7.862 | 0.14286 | 0.92857 | 105.2005 | 0 | 1.3571 |  | 126.9145 | 4.2143 | 267109 | 140 | 52.4131 | 33.9 | 5.9 | 39.8
Residential | 132.281 | 2.7629 | 79.0135 | 2.1339 | 1.4567 | 0 | 50.6041 | 1.885 |  | 261.8986 | 8.2385 | 1013751 | 5183 | 5.1127 | 265.5 | 427 | 692.5
Small Business | 184.9233 | 2.936 | 81.5838 | 2.064 | 1.479 | 0 | 100.62 | 1.6004 |  | 367.1272 | 8.0795 | 73544 | 906 | 12.3192 | 27 | 73.2 | 100.2
General Business -Small | 169.7924 | 3.9929 | 84.8962 | 2.7629 | 2.0053 | 0 | 316.4313 | 1.8717 |  | 571.1199 | 10.6328 | 12957 | 1122 | 86.5941 | 7.4 | 119.3 | 126.7
General Business -Med | 171.7623 | 3.4458 | 76.3359 | 2.1847 | 1.7496 | 0 | 824.4589 | 1.6341 |  | 1072.5571 | 9.0142 | 2911 | 1126 | 386.8087 | 3.1222 | 101.5 | 104.6222
General Business-Large | 207.4689 | 2.7773 | 0 | 0.21364 | 1.4626 | 0 | 1244.8133 | 1.438 |  | 1452.2822 | 5.8915 | 964 | 1217 | 1262.4481 | 1.4 | 71.7 | 73.1
LV >1000kVA | 29600 | 3.9257 | 0 | 0.23873 | 1.7772 | 0 | 1600 | 0.61008 |  | 31200 | 6.5517 | 125 | 377 | 3016 | 3.9 | 24.7 | 28.6
HV less that 1000kVA | 0 | 1.5953 | 0 | 0 | 0 | 0 | 3448.2759 | 0.93385 |  | 3448.2759 | 2.5292 | 116 | 257 | 2215.5172 | 0.4 | 6.5 | 6.9
HV > 1000kVA | 68354.4304 | 1.3465 | 0 | 0 | 0 | 0 | 3797.4684 | 0.21149 |  | 72151.8987 | 1.558 | 316 | 2837 | 8977.8481 | 22.8 | 44.2 | 67
Average | 130.7934 | 2.6307 | 65.513 | 1.4313 | 1.1903 | 20.2521 | 49.0925 | 1.3813 |  | 265.651 | 6.6336 | 1389214 | 13198 | 9.5003 | 369.0461 | 875.5 | 1244.4222
Check
Distribution Network Costs Verses the Implied Network Tariffs
For Customer Groups Used in the Distribution System Cost of Supply
Based on Western Power's 2016/17 Price List Information
| Network Costs |  |  | Implied Network Tariffs
| (Using $/kVA/yr) |  |  | (Using Cents/kWh)
Customer Groups | Dist Total Fixed $/Cust/yr | Dist Total Variable $/kVA/yr |  | Dist Total Fixed $/Cust/yr | Dist Total Variable Cents/kWh
Unreads | 200.907 | 300 |  | 200.907 | 4.5455
Streetlights | 126.9145 | 178.7879 |  | 126.9145 | 4.2143
Residential | 261.8986 | 223.3264 |  | 261.8986 | 8.2385
Small Business | 367.1272 | 217.8571 |  | 367.1272 | 8.0795
General Business -Small | 571.1199 | 215.343 |  | 571.1199 | 10.6328
General Business -Med | 1072.5571 | 207.1429 |  | 1072.5571 | 9.0142
General Business-Large | 1452.2822 | 153.5332 |  | 1452.2822 | 5.8915
LV >1000kVA | 31200 | 147.0238 |  | 31200 | 6.5517
HV less that 1000kVA | 3448.2759 | 103.1746 |  | 3448.2759 | 2.5292
HV > 1000kVA | 72151.8987 | 52.3697 |  | 72151.8987 | 1.558
Average | 265.651 | 179.7003 |  | 265.651 | 6.6336

## New $ per kVA
Develop Tariffs ( $/Customer/yr & $/kVA/yr) for Customer Groups From Revenue Requirement Breakup
But Change Allocation Ratio Between Fixed and Variable Costs from Existing Levels to 70% Fixed and 30% Variable
2016/17 Price List Information Table 10 (Page 24) (Additional Columns and Column Order Altered for Analysis)
| GWh | Customers | ATMD (MVA) | Ave ATMD/ Customer (kVA) | Ave kWh/ Customer | Implied Losses From Zone Sub | LV Only Customers | ATMD Only LV Customers | ATMD - HV Network (MVA) | ATMD Transformers (MVA) | ATMD- LV Network (MVA) | HV Network Fixed ($M) | HV Network Variable ($M) | LV Network Fixed ($M) | LV Network Variable ($M) | Trxs Variable ($M) | Streetlights ($M) | Metering ($M) |  | Admin ($M) | Total ($M)
Unreads | 33 | 17421 | 5 | 0.28701 | 1894.2655 | 16.67% | 17421 | 5 | 6 | 6 | 6 | 2.1 | 0.4 | 1.4 | 0.3 | 0.2 | 0 | 0 |  | 0.6 | 5
Streetlights | 140 | 267109 | 33 | 0.12355 | 524.1306 | 8.333% | 267109 | 33 | 36 | 36 | 4 | 3.7 | 2.5 | 2.1 | 0.2 | 1.3 | 28.1 | 0 |  | 1.9 | 39.8
Residential | 5183 | 1013751 | 1912 | 1.8861 | 5112.6953 | 7.722% | 1013751 | 1912 | 2072 | 2072 | 2072 | 134.1 | 143.2 | 80.1 | 110.6 | 75.5 | 0 | 51.3 |  | 97.7 | 692.5
Small Business | 906 | 73544 | 336 | 4.5687 | 12319.1559 | 4.274% | 73544 | 336 | 351 | 351 | 351 | 13.6 | 26.6 | 6 | 18.7 | 13.4 | 0 | 7.4 |  | 14.5 | 100.2
General Business -Small | 1122 | 12957 | 554 | 42.7568 | 86594.119 | 4.318% | 12957 | 554 | 579 | 579 | 579 | 2.2 | 44.8 | 1.1 | 31 | 22.5 | 0 | 4.1 |  | 21 | 126.7
General Business -Med | 1126 | 2911 | 490 | 168.327 | 386808.6568 | 4.483% | 2620 | 490 | 513 | 513 | 461 | 0.5 | 38.8 | 0.2 | 24.6 | 19.7 | 0 | 2.4 |  | 18.4 | 104.6
General Business-Large | 1217 | 964 | 467 | 484.4398 | 1262448.1328 | 3.313% | 96 | 467 | 483 | 483 | 48 | 0.2 | 33.8 | 0 | 2.6 | 17.8 | 0 | 1.2 |  | 17.5 | 73.1
LV >1000kVA | 377 | 125 | 168 | 1344 | 3016000 | 3.448% | 13 | 168 | 174 | 174 | 17 | 3.7 | 14.8 | 0 | 0.9 | 6.7 | 0 | 0.2 |  | 2.3 | 28.6
HV less that 1000kVA | 257 | 116 | 63 | 543.1034 | 2215517.2414 | 1.562% | 0 | 0 | 64 | 0 | 0 | 0 | 4.1 | 0 | 0 | 0 | 0 | 0.4 |  | 2.4 | 6.9
HV > 1000kVA | 2837 | 316 | 844 | 2670.8861 | 8977848.1013 | 2.088% | 0 | 0 | 862 | 0 | 0 | 21.6 | 38.2 | 0 | 0 | 0 | 0 | 1.2 |  | 6 | 67
Total | 13198 | 1389214 | 4872 | 3.507 | 9500.3362 |  | 1387511 | 3965 | 5140 | 4214 | 3538 | 181.7 | 347.2 | 90.9 | 188.9 | 157.1 | 28.1 | 68.2 |  | 182.3 | 1244.4
Now Recast % Fixed and Variable Components of Total HV & LV Network Costs and Admin Costs | [10 empty] | Total $M |  | 528.9 |  | 279.8 | 157.1 | 28.1 | 68.2 |  | 182.3 | 1244.4
Split Total HV network costs as 70% Fixed (Customer) and 30% Variable (kVA Demand) | [11 empty] | Fixed | Variable | Fixed | Variable | Variable | Fixed | Fixed | Fixed | Variable
Split Total LV network costs as 70% Fixed (Customer) and 30% Variable (kVA Demand) | [10 empty] | % Split | 70% | 30% | 70% | 30% | 100% | 100% | 100% | 70% | 30%
Split Total Administration costs as 70% Fixed (Customer) and 30% Variable (kVA Demand) | [10 empty] | $M Fixed & Variable | 370.23 | 158.67 | 195.86 | 83.94 | 157.1 | 28.1 | 68.2 | 127.61 | 54.69 | 1244.4
Percentage Responsibilty of Costs - Fixed Cost Based on Customer Numbers, Variable Costs Based on ATMD for Cost Type
[11 empty] | % Allocation Based On | Customer Nos | HV ATMD | Customer Nos | LV ATMD | Trx ATMD | Streetlights Only | Metering $M | Customer Nos | Customer ATMD
| GWh | Customers | ATMD (MVA) | Ave ATMD/ Customer (kVA) | Ave kWh/ Customer | Implied Losses From Zone Sub | LV Only Customers | ATMD Only LV Customers | ATMD - HV Network (MVA) | ATMD Transformers (MVA) | ATMD- LV Network (MVA) | HV Network Fixed % Responsible | HV Network Variable % Responsible | LV Network Fixed % Responsible | LV Network Variable % Responsible | Trxs Variable % Responsible | Streetlights Fixed ?? % Responsible | Metering Fixed % Responsible | Admin Fixed % Responsible | Admin Variable % Responsible
Unreads | 33 | 7200 | 5 | 0.69444 | 4583.3333 | 16.67% | 7200 | 5 | 6 | 6 | 6 | 0.6394% | 0.1167% | 0.6404% | 0.1696% | 0.1424% | 0% | 0% | 0.6394% | 0.1026%
Streetlights | 140 | 14200 | 33 | 2.3239 | 9859.1549 | 8.333% | 14200 | 33 | 36 | 36 | 4 | 1.261% | 0.7004% | 1.263% | 0.1131% | 0.8543% | 100% | 0% | 1.261% | 0.6773%
Residential | 5183 | 1013751 | 1912 | 1.8861 | 5112.6953 | 7.722% | 1013751 | 1912 | 2072 | 2072 | 2072 | 90.02% | 40.31% | 90.16% | 58.56% | 49.17% | 0% | 75.22% | 90.02% | 39.24%
Small Business | 906 | 73544 | 336 | 4.5687 | 12319.1559 | 4.274% | 73544 | 336 | 351 | 351 | 351 | 6.531% | 6.829% | 6.541% | 9.921% | 8.329% | 0% | 10.85% | 6.531% | 6.897%
General Business -Small | 1122 | 12957 | 554 | 42.7568 | 86594.119 | 4.318% | 12957 | 554 | 579 | 579 | 579 | 1.151% | 11.26% | 1.152% | 16.37% | 13.74% | 0% | 6.012% | 1.151% | 11.37%
General Business -Med | 1126 | 2911 | 490 | 168.327 | 386808.6568 | 4.483% | 2620 | 490 | 513 | 513 | 461 | 0.2585% | 9.981% | 0.233% | 13.03% | 12.17% | 0% | 3.519% | 0.2585% | 10.06%
General Business-Large | 1217 | 964 | 467 | 484.4398 | 1262448.1328 | 3.313% | 96 | 467 | 483 | 483 | 48 | 0.08561% | 9.397% | 0.008538% | 1.357% | 11.46% | 0% | 1.76% | 0.08561% | 9.585%
LV >1000kVA | 377 | 125 | 168 | 1344 | 3016000 | 3.448% | 13 | 168 | 174 | 174 | 17 | 0.0111% | 3.385% | 0.001156% | 0.4805% | 4.129% | 0% | 0.2933% | 0.0111% | 3.448%
HV less that 1000kVA | 257 | 116 | 63 | 543.1034 | 2215517.2414 | 1.562% | 0 | 0 | 64 | 0 | 0 | 0.0103% | 1.245% | 0% | 0% | 0% | 0% | 0.5865% | 0.0103% | 1.293%
HV > 1000kVA | 2837 | 316 | 844 | 2670.8861 | 8977848.1013 | 2.088% | 0 | 0 | 862 | 0 | 0 | 0.02806% | 16.77% | 0% | 0% | 0% | 0% | 1.76% | 0.02806% | 17.32%
Total | 13198 | 1126084 | 4872 | 4.3265 | 11720.2624 |  | 1124381 | 3965 | 5140 | 4214 | 3538 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
| Customer Nos of Unreads and Streetlights Adjusted to match existing Costs | [6 empty] | There is some inaccuracy in the % Responsibility for customer groups with low ATMDs and ATMDs including losses because of rounding in the data provided
Use Percentage Responsibility of Costs to Determine Each Customer Groups Implied Costs
| GWh | Customers | ATMD (MVA) | Ave ATMD/ Customer (kVA) | Ave kWh/ Customer |  | LV Only Customers | ATMD Only LV Customers |  |  |  | HV Network Fixed ($M) | HV Network Variable ($M) | LV Network Fixed ($M) | LV Network Variable ($M) | Trxs Variable ($M) | Streetlights Fixed ($M) | Metering Fixed ($M) | Admin Fixed % Responsible | Admin Variable ($M) | Total ($M)
Total $M | [11 empty] | 370.23 | 158.67 | 195.86 | 83.94 | 157.1 | 28.1 | 68.2 | 127.61 | 54.69 | 1244.4
Unreads | 33 | 7200 | 5 | 0.69444 | 4583.3333 |  | 7200 | 5 |  |  |  | 2.3672 | 0.18522 | 1.2542 | 0.14235 | 0.22368 | 0 | 0 | 0.81592 | 0.056127 | 5.0447
Streetlights | 140 | 14200 | 33 | 2.3239 | 9859.1549 |  | 14200 | 33 |  |  |  | 4.6686 | 1.1113 | 2.4735 | 0.094901 | 1.3421 | 28.1 | 0 | 1.6092 | 0.37044 | 39.7701
Residential | 5183 | 1013751 | 1912 | 1.8861 | 5112.6953 |  | 1013751 | 1912 |  |  |  | 333.2975 | 63.9619 | 176.589 | 49.1588 | 77.2452 | 0 | 51.3 | 114.8802 | 21.4629 | 887.8955
Small Business | 906 | 73544 | 336 | 4.5687 | 12319.1559 |  | 73544 | 336 |  |  |  | 24.1795 | 10.8352 | 12.8109 | 8.3276 | 13.0855 | 0 | 7.4 | 8.3341 | 3.7717 | 88.7446
General Business -Small | 1122 | 12957 | 554 | 42.7568 | 86594.119 |  | 12957 | 554 |  |  |  | 4.26 | 17.8735 | 2.257 | 13.7369 | 21.5854 | 0 | 4.1 | 1.4683 | 6.2189 | 71.5
General Business -Med | 1126 | 2911 | 490 | 168.327 | 386808.6568 |  | 2620 | 490 |  |  |  | 0.95707 | 15.8361 | 0.45639 | 10.9373 | 19.1249 | 0 | 2.4 | 0.32988 | 5.5004 | 55.5421
General Business-Large | 1217 | 964 | 467 | 484.4398 | 1262448.1328 |  | 96 | 467 |  |  |  | 0.31694 | 14.91 | 0.016723 | 1.1388 | 18.0065 | 0 | 1.2 | 0.10924 | 5.2422 | 40.9405
LV >1000kVA | 377 | 125 | 168 | 1344 | 3016000 |  | 13 | 168 |  |  |  | 0.041097 | 5.3713 | 0.0022645 | 0.40333 | 6.4868 | 0 | 0.2 | 0.014165 | 1.8859 | 14.4048
HV less that 1000kVA | 257 | 116 | 63 | 543.1034 | 2215517.2414 |  | 0 | 0 |  |  |  | 0.038138 | 1.9757 | 0 | 0 | 0 | 0 | 0.4 | 0.013145 | 0.7072 | 3.1341
HV > 1000kVA | 2837 | 316 | 844 | 2670.8861 | 8977848.1013 |  | 0 | 0 |  |  |  | 0.10389 | 26.6096 | 0 | 0 | 0 | 0 | 1.2 | 0.03581 | 9.4742 | 37.4236
Total | 13198 | 1126084 | 4872 | 4.3265 | 11720.2624 |  | 1124381 | 3965 |  |  |  | 370.23 | 158.67 | 195.86 | 83.94 | 157.1 | 28.1 | 68.2 | 127.61 | 54.69 | 1244.4
Determine the Fixed ( $/Customer/yr) and Variable ($/kVA) Costs for Each Customer at their Meter (The $/kVA will vary due to the line losses)
| GWh | Customers | ATMD All Customers (MVA) | Ave ATMD/ Customer (kVA) | Ave kWh/ Customer |  | LV Only Customers | ATMD LV Ony Customers (MVA) |  |  |  | HV Fixed $/Cust/yr | HV Variable $/kVA/yr Metered | LV Fixed $/Cust/yr | LV Variable $/ kVA/yr Metered | Trxs Variable $/kVA/yr Metered | Streetlights $/Cust/yr ??? | Metering $/Cust/yr | Admin $/Cust/yr | Admin $/kVA/yr Metered | Total Network $/Cust/yr | Total Network $/kVA/yr Metered
Unreads | 33 | 7200 | 5 | 0.69444 | 4583.3333 |  | 7200 | 5 |  |  |  | 328.7765 | 37.0436 | 174.1936 | 28.4703 | 44.7366 | 0 | 0 | 113.3219 | 11.2254 | 616.2921 | 121.4759
Streetlights | 140 | 14200 | 33 | 2.3239 | 9859.1549 |  | 14200 | 33 |  |  |  | 328.7765 | 33.676 | 174.1936 | 2.8758 | 40.6696 | 1978.8732 | 0 | 113.3219 | 11.2254 | 2595.1653 | 88.4468
Residential | 5183 | 1013751 | 1912 | 1.8861 | 5112.6953 |  | 1013751 | 1912 |  |  |  | 328.7765 | 33.4529 | 174.1936 | 25.7106 | 40.4002 | 0 | 50.6041 | 113.3219 | 11.2254 | 666.8962 | 110.7891
Small Business | 906 | 73544 | 336 | 4.5687 | 12319.1559 |  | 73544 | 336 |  |  |  | 328.7765 | 32.2478 | 174.1936 | 24.7844 | 38.9448 | 0 | 100.62 | 113.3219 | 11.2254 | 716.9121 | 107.2024
General Business -Small | 1122 | 12957 | 554 | 42.7568 | 86594.119 |  | 12957 | 554 |  |  |  | 328.7765 | 32.2627 | 174.1936 | 24.7959 | 38.9628 | 0 | 316.4313 | 113.3219 | 11.2254 | 932.7234 | 107.2468
General Business -Med | 1126 | 2911 | 490 | 168.327 | 386808.6568 |  | 2620 | 490 |  |  |  | 328.7765 | 32.3186 | 174.1936 | 22.3211 | 39.0304 | 0 | 824.4589 | 113.3219 | 11.2254 | 1440.751 | 104.8955
General Business-Large | 1217 | 964 | 467 | 484.4398 | 1262448.1328 |  | 96 | 467 |  |  |  | 328.7765 | 31.9273 | 174.1936 | 2.4386 | 38.5578 | 0 | 1244.8133 | 113.3219 | 11.2254 | 1861.1054 | 84.149
LV >1000kVA | 377 | 125 | 168 | 1344 | 3016000 |  | 13 | 168 |  |  |  | 328.7765 | 31.9721 | 174.1936 | 2.4008 | 38.6119 | 0 | 1600 | 113.3219 | 11.2254 | 2216.2921 | 84.2102
HV less that 1000kVA | 257 | 116 | 63 | 543.1034 | 2215517.2414 |  | 0 | 0 |  |  |  | 328.7765 | 31.3596 | 0 | 0 | 0 | 0 | 3448.2759 | 113.3219 | 11.2254 | 3890.3743 | 42.585
HV > 1000kVA | 2837 | 316 | 844 | 2670.8861 | 8977848.1013 |  | 0 | 0 |  |  |  | 328.7765 | 31.528 | 0 | 0 | 0 | 0 | 3797.4684 | 113.3219 | 11.2254 | 4239.5668 | 42.7534
Total | 13198 | 1126084 | 4872 | 4.3265 | 11720.2624 |  | 1124381 | 3965 |  |  | Average | 328.7765 | 32.5677 | 174.1936 | 21.1702 | 39.6217 | 0 | 60.5639 | 113.3219 | 11.2254 | 676.8559 | 104.585
Check Prices give Revenue Requirement ie $/Cust/yr Mulitplied by Customer Numbers and Customer Group ATMD KVA multiplied by $/kVA/yr
| GWh | Customers | ATMD All Customers (MVA) | Ave ATMD/ Customer (kVA) | Ave kWh/ Customer |  | LV Only Customers |  |  |  |  | HV Network Fixed ($M) | HV Network Variable ($M) | LV Network Fixed ($M) | LV Network Variable ($M) | Trxs Variable ($M) | Streetlights ($M) | Metering ($M) | Admin Fixed ($M) | Admin Variable ($M) | Total ($M)
Unreads | 33 | 7200 | 5 | 0.69444 | 4583.3333 |  | 7200 |  |  |  |  | 2.3672 | 0.18522 | 1.2542 | 0.14235 | 0.22368 | 0 | 0 | 0.81592 | 0.056127 | 5.0447
Streetlights | 140 | 14200 | 33 | 2.3239 | 9859.1549 |  | 14200 |  |  |  |  | 4.6686 | 1.1113 | 2.4735 | 0.094901 | 1.3421 | 28.1 | 0 | 1.6092 | 0.37044 | 39.7701
Residential | 5183 | 1013751 | 1912 | 1.8861 | 5112.6953 |  | 1013751 |  |  |  |  | 333.2975 | 63.9619 | 176.589 | 49.1588 | 77.2452 | 0 | 51.3 | 114.8802 | 21.4629 | 887.8955
Small Business | 906 | 73544 | 336 | 4.5687 | 12319.1559 |  | 73544 |  |  |  |  | 24.1795 | 10.8352 | 12.8109 | 8.3276 | 13.0855 | 0 | 7.4 | 8.3341 | 3.7717 | 88.7446
General Business -Small | 1122 | 12957 | 554 | 42.7568 | 86594.119 |  | 12957 |  |  |  |  | 4.26 | 17.8735 | 2.257 | 13.7369 | 21.5854 | 0 | 4.1 | 1.4683 | 6.2189 | 71.5
General Business -Med | 1126 | 2911 | 490 | 168.327 | 386808.6568 |  | 2620 |  |  |  |  | 0.95707 | 15.8361 | 0.45639 | 10.9373 | 19.1249 | 0 | 2.4 | 0.32988 | 5.5004 | 55.5421
General Business-Large | 1217 | 964 | 467 | 484.4398 | 1262448.1328 |  | 96 |  |  |  |  | 0.31694 | 14.91 | 0.016723 | 1.1388 | 18.0065 | 0 | 1.2 | 0.10924 | 5.2422 | 40.9405
LV >1000kVA | 377 | 125 | 168 | 1344 | 3016000 |  | 13 |  |  |  |  | 0.041097 | 5.3713 | 0.0022645 | 0.40333 | 6.4868 | 0 | 0.2 | 0.014165 | 1.8859 | 14.4048
HV less that 1000kVA | 257 | 116 | 63 | 543.1034 | 2215517.2414 |  | 0 |  |  |  |  | 0.038138 | 1.9757 | 0 | 0 | 0 | 0 | 0.4 | 0.013145 | 0.7072 | 3.1341
HV > 1000kVA | 2837 | 316 | 844 | 2670.8861 | 8977848.1013 |  | 0 |  |  |  |  | 0.10389 | 26.6096 | 0 | 0 | 0 | 0 | 1.2 | 0.03581 | 9.4742 | 37.4236
Total | 13198 | 1126084 | 4872 | 4.3265 | 11720.2624 |  | 1124381 |  |  |  |  | 370.23 | 158.67 | 195.86 | 83.94 | 157.1 | 28.1 | 68.2 | 127.61 | 54.69 | 1244.4
Compare Western Power Network Implied Tariff with Tariff developed based upon Higher Fixed Cost allocation
The Proposed Network Tariff Structure (with a Higher Fixed Cost Allocation)
in Comparison to the Existing Network Cost Structure (Based upon kVA Demand)
| Existing Network Costs |  |  | Proposed Network Tariffs |  |  | % Difference
% Allocation to Fixed & Variable | Existing | Existing |  | 70% | 30%
| Customer Group (Fixed) $/Cust/yr | Customer Group (Variable) $/kVA/yr |  | Customer Group (Fixed) $/Cust/yr | Customer Group (Variable) $/kVA/yr |  | % Difference in Fixed $/Cust/yr | % Difference in Variable $/kVA/yr
Unreads | 200.907 | 300 |  | 616.2921 | 121.4759 | Note 1 | 306.8% | 40.49%
Streetlights | 126.9145 | 178.7879 |  | 2595.1653 | 88.4468 | Note 1 | 2045% | 49.47%
Residential | 261.8986 | 223.3264 |  | 666.8962 | 110.7891 |  | 254.6% | 49.61%
Small Business | 367.1272 | 217.8571 |  | 716.9121 | 107.2024 |  | 195.3% | 49.21%
General Business -Small | 571.1199 | 215.343 |  | 932.7234 | 107.2468 |  | 163.3% | 49.8%
General Business -Med | 1072.5571 | 207.1429 |  | 1440.751 | 104.8955 |  | 134.3% | 50.64%
General Business-Large | 1452.2822 | 153.5332 |  | 1861.1054 | 84.149 |  | 128.2% | 54.81%
LV >1000kVA | 31200 | 147.0238 |  | 2216.2921 | 84.2102 |  | 7.104% | 57.28%
HV less that 1000kVA | 3448.2759 | 103.1746 |  | 3890.3743 | 42.585 |  | 112.8% | 41.27%
HV > 1000kVA | 72151.8987 | 52.3697 |  | 4239.5668 | 42.7534 |  | 5.876% | 81.64%
Average | 253.3412 | 196.5474 |  | 676.8559 | 104.585 |  | 267.2% | 53.21%
Note 1 : Unreads and Streetlight customer numbers adjusted to give the same network revenue

## Cable & Line Cust & kVA Cost
Examine Fixed and Variable Percentages of Total Underground Cable and Overhead Line Costs
Based on Western Power Corporation Network Assets Valuation as at 30 June 2004
Underground HV Cables ( Fully Installed) | Capacity Catalogue (A) | Derating Factor | Capacity WA Conditions (A) | Cable kVA Rating | Installed Cost $/ km | Ave Cost per kVA | Incremental kVA | Incremental Cost | Incremental Cost per kVA
22kV U/G Light ( 35mm2 Al) Min Cable Size | 135 | 0.8 | 108 | 4115.3527 | 67545 | 16.4129
22kV U/G Medium (95mm2 Al) | 230 | 0.8 | 184 | 7011.3417 | 73998 | 10.554 | 2895.989 | 6453 | 2.2283
22kV U/G Standard (185mm2 Al) | 330 | 0.8 | 264 | 10059.7511 | 84994 | 8.4489 | 3048.4094 | 10996 | 3.6071
Fixed vs Variable Components of the Installed Cost of 22kV Underground Cables
| Installed Cable Cost $ per km | % Total Cost | Cable kVA Capacity | Delta kVA | Incremental $/kVA/km
Cost of 22kV U/G ( 35mm2 Al) Min Size Cable | 67545 | 79.47% | 4115.3527
Variable Cost - Additional Cost to 185mm2 | 17449 | 20.53% |  | 5944.3984 | 2.9354
Cost of 22kV U/G (185mm2 Al) Cable | 84994 |  | 10059.7511
Based on Western Power Corporation Network Assets Valuation as at 30 June 2004
Overhead 3 Phase Lines ( Fully Installed) |  |  | Capacity Summer Still Air (A) | Line Capacity kVA | Installed Cost ($/ km) | Ave Cost per kVA | Incremental kVA | Incremental Cost | Incremental Cost per kVA/km
22kV 7/2.50 AAAC, 40m Bays (35mm2) | Min Size |  | 93 | 3543.776 | 47170 | 13.3107
22kV 7/4.75 AAAC, 40m Bays (124mm2) |  |  | 207 | 7887.7594 | 50289 | 6.3756 | 4343.9834 | 3119 | 0.718
22kV 19/3.25 AAAC, 40m Bays (158mm2) |  |  | 240 | 9145.2283 | 50981 | 5.5746 | 1257.4689 | 692 | 0.55031
| Cost per km | % Total Cost | Delta kVA | $/kVA Incremental Cost
Fixed Cost (Min O/H Line ) Irrespective of kVA | 47170 | 92.52%
Variable Cost - Additional Cost to 185mm2 | 3811 | 7.475% | 5601.4523 | 0.68036
Total Cost | 50981

## Solar Impact Network Rev
Estimate Additional Network Costs Retailers have Incurred due to Residential Solar
As a result of Western Power charging Cents/kWh
Forecast Tariff Customer Data From WPC Price List Information
2007/08 | kWh | ATMD (kVA) | Customers | Ave kWh/Cust | Ave ATMD /Cust | Ld Fact
RT1 - Anytime Energy Residential | 4635699431 | 1633296 | 796776 | 5818.0711 | 2.0499 | 32.4%
RT3- TOU Energy Residential | 149991483 | 52105 | 15076 | 9949.0238 | 3.4562 | 32.86%
Total | 4785690914 | 1685401 | 811852 | 5894.7824 | 2.076 | 32.41%
2008/09 | kWh | ATMD (kVA) | Customers | Ave kWh/Cust | Ave ATMD /Cust | Ld Fact
RT1 - Anytime Energy Residential | 4783329262 | 1682894 | 801690 | 5966.5572 | 2.0992 | 32.45%
RT3- TOU Energy Residential | 252860560 | 96946 | 18902 | 13377.45 | 5.1289 | 29.77%
Total | 5036189822 | 1779840 | 820592 | 6137.2641 | 2.169 | 32.3%
2009/10 | kWh | ATMD (kVA) | Customers | Ave kWh/Cust | Ave ATMD /Cust | Ld Fact
RT1 - Anytime Energy Residential | 5112296250 | 0 | 856826 | 5966.5513 | 0 | #DIV/0!
RT3- TOU Energy Residential | 159593976 | 0 | 15797 | 10102.8028 | 0 | #DIV/0! | PV Customers and Ave PV Size From
Total | 5271890226 | 0 | 872623 | 6041.4294 | 0 | #DIV/0! | 2017 Electricity Statement of Opportunities
|  |  |  | Use as Benchmark Without PV |  |  | Published by AEMO for WEM 15/6/17
2010/11 | kWh | ATMD (kVA) | Customers | Ave kWh/Cust | Ave ATMD /Cust | Ld Fact |  | Number of PV Customers | Average PV Size (kW)
RT1 - Anytime Energy Residential | 5101287006 | 1787914 | 825867 | 6176.8868 | 2.1649 | 32.57%
RT3- TOU Energy Residential | 172417706 | 61980 | 15744 | 10951.3279 | 3.9367 | 31.76% |  | 69813 | 2.1
Total | 5273704712 | 1849894 | 841611 | 6266.2022 | 2.198 | 32.54%
2011/12 | kWh | ATMD (kVA) | Customers | Ave kWh/Cust | Ave ATMD /Cust | Ld Fact
RT1 - Anytime Energy Residential | 5566407460 | 2238840 | 861104 | 6464.2685 | 2.6 | 28.38%
RT3- TOU Energy Residential | 193825856 | 79491 | 19537 | 9920.9631 | 4.0687 | 27.83%
Total | 5760233316 | 2318331 | 880641 | 6540.9552 | 2.6325 | 28.36% |  | 94893 | 2.2
2012/13 | kWh | ATMD (kVA) | Customers | Ave kWh/Cust | Ave ATMD /Cust | Ld Fact
RT1 - Anytime Energy Residential | 5319275949 | 2158583 | 928361 | 5729.7495 | 2.3252 | 28.13%
RT3- TOU Energy Residential | 213268785 | 87672 | 24799 | 8599.8946 | 3.5353 | 27.77%
Total | 5532544734 | 2246255 | 953160 | 5804.424 | 2.3566 | 28.12% |  | 119081 | 2.4
2013/14 | kWh | ATMD (kVA) | Customers | Ave kWh/Cust | Ave ATMD /Cust | Ld Fact
RT1 - Anytime Energy Residential | 5038293501 | 1910401 | 937026 | 5376.8983 | 2.0388 | 30.11%
RT3- TOU Energy Residential | 186995311 | 72254 | 22897 | 8166.804 | 3.1556 | 29.54%
Total | 5225288812 | 1982655 | 959923 | 5443.4458 | 2.0654 | 30.09% |  | 138307 | 2.6
2014/15 | kWh | ATMD (kVA) | Customers | Ave kWh/Cust | Ave ATMD /Cust | Ld Fact
RT1 - Anytime Energy Residential | 4930045113 | 2180790 | 920862 | 5353.7285 | 2.3682 | 25.81%
RT3- TOU Energy Residential | 151774109 | 70448 | 21869 | 6940.1486 | 3.2214 | 24.59%
Total | 5081819222 | 2251238 | 942731 | 5390.5295 | 2.388 | 25.77% |  | 161205 | 2.7
2015/16 | kWh | ATMD (kVA) | Customers | Ave kWh/Cust | Ave ATMD /Cust | Ld Fact
RT1 - Anytime Energy Residential | 5040980245 | 1970869 | 927656 | 5434.1051 | 2.1246 | 29.2%
RT3- TOU Energy Residential | 159278898 | 63877 | 21594 | 7376.072 | 2.9581 | 28.46%
Total | 5200259143 | 2034746 | 949250 | 5478.282 | 2.1435 | 29.17% |  | 181125 | 2.9
2016/17 | kWh | ATMD (kVA | Customers | Ave kWh/Cust | Ave ATMD /Cust | Ld Fact
RT1 - Anytime Energy Residential | 4174639051 | 1535216 | 821915 | 5079.1615 | 1.8679 | 31.04% |  | Estimated
RT3- TOU Energy Residential | 89022785 | 29160 | 10369 | 8585.4745 | 2.8122 | 34.85% |  | kW/Cust | 3.3 | kW
RT13- Anytime Energy Resid Bi-Direct | 858017650 | 320913 | 171809 | 4994.0204 | 1.8678 | 30.52% |  | for 2016/17
RT15- TOU Resid Bi-Directional | 61727979 | 27162 | 9658 | 6391.3832 | 2.8124 | 25.94%
Total | 5183407465 | 1912451 | 1013751 | 5113.0973 | 1.8865
Estimated Solar PV Impact on Network Metered kWh for 2016/17 |  |  | Customers | Ave Network Metered kWh/Cust | Network Metered kWh | Ave Metered kWh Reduction of Customer with Solar PV | Assumed PV Load Factor for Avoided Metered kWh | Calculated Ave Solar kW/Cust
Residential Total No Solar (2009/10 kWh/Cust x 2016/17 Cust Nos) |  |  | 1013751 | 6041 | 6124069791
Residential Total With Solar (2015/16 kWh/Cust x 2016/17 Cust Nos) |  |  | 1013751 | 5478 | 5553327978
Difference = Theoretical Solar Production |  |  | 181467 |  | 570741813 | 3145.1548 | 11% | 3.264
(Note 2015/16 kWh/Cust used as 2016/17 kWh/Cust seems too low) | [5 empty] | (This appears reasonable given
typical PV Total Load Factor above 20%)
|  |  |  | Cents/kWh | kWh | $M /Annum
Loss of Network Revenue from Customers Taking Up Solar |  |  |  | 8.744 | 570741813 | 49.9057